## Slide 1
House of Resistance - Subs

## Slide 2
gpm
Pumping level
Elevation
ft.
ft.
things to know to select a pump
Zone 4
dp
5
How it works is simple…
fill in five blanks.
As the blanks get filled-in, explanation will be provided for each “room” in the house, so you know what to look for.
Pressure
psi
Friction
psi
(loss)

## Slide 3
Zone 4
gallons per minute
Represents the maximum flow rate (gpm) required of the pump.
Submersible Pumps can have broad applications
● Irrigation System
● Home Water System
● Home & Irrigation (both)
various applications will determine the maximum flow rate (gpm).

## Slide 4
Zone 4
Home Water System
Fixture Count Method
The total number of fixtures in the house should equal the gpm rating of the pump.
Kitchen
● Sink
● Dishwasher
Laundry Room
● Clothes Washer
● Laundry Tub Sink
Full Bath
● Tub/Shower
● Lavatory
● Toilet
½ Bath
● Lavatory
● Toilet
● Outside Hose Bibb
2
2
2
3
+___
1
total fixtures
10 gpm Maximum Flow Rate
10
10

## Slide 5
Zone 4
Irrigation System (only)
Zone 1
9 gpm
Zone 2
18 gpm
Zone 3
15 gpm
Zone 5
9 gpm
Zone 4
21 gpm
(7 Rotors)
Maximum Flow Rate

## Slide 6
Home Water System and Irrigation
Zone 4
21 gpm
10 gpm
≈25 gpm

## Slide 7
Zone 4
Application

## Slide 8
gallons per minute
25

## Slide 9
Zone 4
25
Pressure (psi)
Represents the maximum pressure (psi) required of the pump.
Irrigation
home water systems
50psi - 65psi
20psi - 45psi
50

## Slide 10
A few things before Pumping Level
Typical well records / logs will include such information as…
◦ Well location
◦ Well Depth
◦ Well Diameter
◦ Geologic formations
◦ Well Yield (gpm or gph)
◦ Static Water Level
25
50

## Slide 11
Distance from the surface to water level in well, under non-pumping, undisturbed conditions.
Static Water Level
if less than 25 feet Shallow Well
if more than 25 feet Deep Well
Surface
25
50
Static Water Level
(ft.)

## Slide 12
Static Water Level
Static Water Level
Surface
Drawdown (ft.)
Drawdown
25
50
Distance from the surface to water level in well while the pump is running.

## Slide 13
Surface
Pumping Level
Pumping Level
Where the pump will set.
58
25
50
(ft.)
is a portion of the “resistance” that the pump must overcome.

## Slide 14
Elevation (ft.)
Surface
25
50
58
the vertical distance from the surface to highest point in the irrigation system
Irrigation System
Home Water System
the vertical distance from the surface to the pressure tank.
Example: 6 feet
6

## Slide 15
Friction – (psi loss)
25
50
58
6
occurs anytime two surfaces pass by one another
Use Friction Loss Charts to calculate (psi loss)
To determine how much pressure we’re going lose due to friction

## Slide 16
Zone 1 3 Rotors
Zone 2 6 Rotors
Zone 4 7 Rotors
Zone 5 3 Rotors
How to read a Friction Loss chart
25
50
58
6
Flow Rate
(gpm)
what you need to know
50’
100’
150’
200’
250’
300’
350’
400’
500’
0.75”
1.00”
1.25”
1.50”
2.00”
PVC/SCH 40
PVC/SCH 80
PVC/SCH 120
POLY
SDR-21
SDR-26
SCH 40 Steel
Pipe Length
Pipe Type
Pipe Size
25 gpm

## Slide 17
Pipe Type
Pipe Size
Flow Rate
(gpm)
Pressure
(psi loss)
25 gpm flowing through 1.25” pipe, will lose 3.56 psi per 100’ of pipe
Lose about 3½ psi per 100 ft. of 1¼” pipe
Lose about 9 psi in 250 feet of 1¼” pipe
Velocity
(feet/sec)
25 gpm flowing through 1.25” pipe, will move at a speed of 5.47 feet per second, per 100’ of pipe
Friction Loss
9 psi

## Slide 18
Friction – (psi loss)
25
50
58
6
Friction Loss
9 psi
9

## Slide 19
25
50
58
6
9
The House contains all the resistance that the pump will need to overcome
Add up the total number of feet in house.
Convert pressure (psi) to feet (ft.)

## Slide 20
25
50
58
6
9
The House contains all the resistance that the pump will need to overcome
Converting Pressure (psi) to Feet (ft)
x 2.31=
50 X 2.31 =
115.5 (116 ft.)

## Slide 21
Converting Pressure (psi) to Feet (ft)
25
50
58
6
9
9 X 2.31 =
20.79 (21 ft.)
x 2.31=

## Slide 22
Why x 2.31 ?
1 ft
2 ft
3 ft
(116 x .433 = 50.01 psi)
to convert feet to psi
x .433
____ feet x .433 = psi
2.31 feet
1 psi
25
58
6

## Slide 23
add-up the rooms
Pressure
Friction
Pumping level
Elevation
201 ft.
Total
116 ft.
58 ft.
6 ft.
21 ft.
+________

## Slide 24
add-up the rooms
Pressure
Friction
116 ft.
58 ft.
6 ft.
21 ft.
Pumping level
Elevation
Total
+________
these two numbers
25
201 ft.
Gallons per minute
Feet

## Slide 25
25
Gallons per minute
Feet
these two numbers
Are all you need to read a pump curve and size the pump!
As your applications change, the house will always provide you with the two numbers.
a.k.a.
Total Dynamic Head
(TDH)
201 ft.
Gallons per minute
Feet

## Slide 26
these two numbers
Gallons per minute
Feet
How to read a pump curve

## Slide 27
Gallons per minute
Feet
How to read a pump curve

## Slide 28
How to read a pump curve
Feet (ft.)
gallons per minute (gpm)

## Slide 29
How to read a pump curve
Overload the motor
Overload the pump

## Slide 30
How to read a pump curve
resistance
1½ hp 27gpm Sub
25 gpm @ 201’
2hp 27gpm Sub
29 gpm @ 201’

## Slide 31
How to read a pump curve
2hp 27gpm Sub
25 gpm @ 250’
resistance

## Slide 32
How to read a pump curve

## Slide 33
How to read a pump curve
2hp 19gpm Sub
17 gpm @ 350’

## Slide 34
Zone 4
House of Resistance - Subs
dp
…a non-traditional way to pump sizing
so there you have it…

## Slide 35
https://www.youtube.com/@flintandwalling
subscribe