## Slide 1
Testing Submersible Motors w/ Meters & Meggers
track 1A

## Slide 2
w/ Meters
& Meggers
Testing Submersible Motors

## Slide 3
w/ Meters
& Meggers
Meters measure resistance and displays it in “ohms”
No resistance equals “0” Ohms
“0” Ohms equals “Infinity”
Infinity, dependent upon meter, will be displayed one of two ways
Infinity
Testing Submersible Motors

## Slide 4
Two types of meters
Analog
Digital
an adjustable scale, set prior to taking the measurement.
a dial to “zero” out the meter.
have auto-ranging features,
no need to zero-out

## Slide 5
w/ Meters
Testing Submersible Motors
Lead Identification
Short
Open Winding
Mixed Leads
Ground
Cut Power to pressure switch / motor

## Slide 6
w/ Meters
Testing Submersible Motors
Lead Identification
Short
Open Winding
Mixed Leads
Ground

## Slide 7
Motor Types
3W Motors
2W Motors
Start Winding
Run Winding
Common
Ground
Ground
Lead A
Lead B

## Slide 8
w/ Meters
Testing Submersible Motors
Ground
Short
Open Winding
Mixed Leads
Lead Identification

## Slide 9
Mixed Leads
Open Winding
Short
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Lead Identification
Each Lead to Lead
?

## Slide 10
ohms

## Slide 11
M 1.7 – 2.2
A 7.8 – 9.6
(Yellow to Black)
(Yellow to Red)
ohms
ohms

## Slide 12
1½ hp 3-wire motor

## Slide 13
+_________
1½ hp 3-wire motor
Common / Run
Common / Start
Start / Run
Intermediate Value
Lowest Value
Highest Value
+
=

## Slide 14
w/ Meters
Testing Submersible Motors
Short
Open Winding
Mixed Leads
Ground
Lead Identification
Yellow / Black
Yellow / Red
Red / Black

## Slide 15
w/ Meters
Testing Submersible Motors
Ground
Short
Open Winding
Mixed Leads
Lead Identification

## Slide 16
1½ hp 3-wire motor
OL.
1.8
1.7
Resistance Value
is Lower than published values

## Slide 17
Resistance Value
is Lower than published values
coming in “SHORT”
Published Values

## Slide 18
Mixed Leads
Open Winding
Short
Lead Identification
Within Range
Motor not shorted
Lower than Range
Motor shorted
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead

## Slide 19
1½ hp 3-wire motor
1.7
(Red to Black)
Red
Red

## Slide 20
w/ Meters
Testing Submersible Motors
Ground
Open Winding
Mixed Leads
Lead Identification
Short

## Slide 21
1½ hp 3-wire motor
OL.
8.0
9.4
Resistance Value
is Higher than published values

## Slide 22
OPEN
Up
Resistance Value
is Higher than published values

## Slide 23
1½ hp 3-wire motor
9.4
(Red to Black)
(Red to Black)
(Yellow to Black)

## Slide 24
Mixed Leads
Open Winding
Short
Lead Identification
Within Range
Motor not shorted
Lower than Range
Motor shorted
Within Range
Windings not open
Higher than Range
Open Windings
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead

## Slide 25
w/ Meters
Testing Submersible Motors
Ground
Mixed Leads
Short
Lead Identification
Open Winding

## Slide 26
1½ hp 3-wire motor
OL.
8.0
1.9
Mixed Leads

## Slide 27
1½ hp 3-wire motor
Mixed Leads
…lead socket?
…Check Splice

## Slide 28
Mixed Leads
Open Winding
Short
Lead Identification
Within Range
Motor not shorted
Lower than Range
Motor shorted
Within Range
Windings not open
Higher than Range
Open Windings
Within Ranges
No mixed leads
Higher / Lower
Mixed Leads
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead

## Slide 29
w/ Meters
Testing Submersible Motors
Short
Lead Identification
Open Winding
Mixed Leads
Ground

## Slide 30
Mixed Leads
Open Winding
Short
Lead Identification
Within Range
Motor not shorted
Lower than Range
Motor shorted
Within Range
Windings not open
Higher than Range
Open Windings
Within Ranges
No mixed leads
Higher / Lower
Mixed Leads
Ground
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each
Lead to Ground

## Slide 31
1½ hp 3-wire motor
OL.
0.2
No resistance –
Motor not grounded
Any resistance at all–
Motor is grounded

## Slide 32
1½ hp 3-wire motor
0.2
A grounded motor in most cases, will show resistance on every lead.
If you test an old motor that doesn’t have a ground…
use the well casing or the S.S. motor shell to provide ground.

## Slide 33
Mixed Leads
Open Winding
Short
Lead Identification
Within Range
Motor not shorted
Lower than Range
Motor shorted
Within Range
Windings not open
Higher than Range
Open Windings
Within Ranges
No mixed leads
Higher / Lower
Mixed Leads
Ground
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each Lead to Lead
Each
Lead to Ground
No resistance
Motor not grounded
Any resistance
Motor grounded

## Slide 34
w/ Meters
Testing Submersible Motors
Short
Lead Identification
Open Winding
Mixed Leads
Ground

## Slide 35
w/ Meters
Testing Submersible Motors

## Slide 36
w/ Meters
Testing Submersible Motors
within specified range / good.
Take-a-ways
Short
Open
Leads
Mixed

## Slide 37
w/ Meters
& Meggers
Testing Submersible Motors

## Slide 38
& Meggers
Testing Submersible Motors
Insulation
Resistance

## Slide 39
500 -1000 volts
megohms
MΩ
w/ Meters
Testing Submersible Motors
& Meggers
ohms
Ω
1,000,000 ohms equals…
1 megohm
1-9 volts
This test will determine the condition of the outer coating of the wire.
Is essential to keeping wires & motors working properly.

## Slide 40
Test for insulation resistance
Meggers
nicks, thin insulation
cracks, pin holes, wear

## Slide 41
Test for insulation resistance
Meggers
nicks, thin insulation
cracks, pin holes, wear
windings
degrade over time

## Slide 42
Test for insulation resistance
Meggers
windings
degrade over time
Is copper wire and magnet wire the same?
Both use a copper conductor. However, magnet copper wire has a thin high heat absorbing special coating or insulation (like an enamel or varnish)
This insulation protects the windings from contamination, shorting electrically.

## Slide 43
Test for insulation resistance
Meggers
…good or bad?
…measure each
lead to ground
NEW MOTOR
USED MOTOR
20MΩ or more
10MΩ or more
If below above values… do not install
2MΩ or more
0.5MΩ or more
If below above values… do not install
NEW MOTOR
USED MOTOR
In the well Out of well

## Slide 44
w/ Meters
& Meggers
Testing Submersible Motors

## Slide 45
w/ Meters
& Meggers
Testing Submersible Motors
…will have very similar Insulation Resistance values.
Motors of all horsepower, voltage & phase…
Motors should be placed on a non-conductive surface when testing motor out of the well..

## Slide 46
Testing Submersible Motors w/ Meters & Meggers
track 1A
thank you