## Slide 1
CommanderPro® Variable Frequency drives

## Slide 2
COMMANDER PRO VFD
TVS15
TVS20
TVS30
3 wire three phase
& 3 wire single phase

## Slide 3
COMMANDER PRO INITIAL SETUP

## Slide 4
COMMANDER PRO INITIAL SETUP

## Slide 5
COMMANDER PRO INITIAL SETUP

## Slide 6
COMMANDER PRO INITIAL SETUP

## Slide 7
COMMANDER PRO INITIAL SETUP

## Slide 8
COMMANDER PRO INITIAL SETUP

## Slide 9
COMMANDER PRO INITIAL SETUP

## Slide 10
COMMANDER PRO INITIAL SETUP
¾ HP 1 HP 1½ HP 2 HP
8.0 10.4 11.5 13.2

## Slide 11
COMMANDER PRO INITIAL SETUP

## Slide 12
COMMANDER PRO INITIAL SETUP

## Slide 13
COMMANDER PRO INITIAL SETUP

## Slide 14
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
COMMANDER PRO MENU OPTIONS

## Slide 15
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
COMMANDER PRO MENU OPTIONS

## Slide 16
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
COMMANDER PRO MENU OPTIONS

## Slide 17
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
COMMANDER PRO MENU OPTIONS

## Slide 18
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
COMMANDER PRO MENU OPTIONS

## Slide 19
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
COMMANDER PRO MENU OPTIONS

## Slide 20
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
7. Broken Pipe
  (1/2 – 48) Hours
COMMANDER PRO MENU OPTIONS

## Slide 21
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
7. Broken Pipe
  (1/2 – 48) Hours
8. Advanced Features
COMMANDER PRO MENU OPTIONS

## Slide 22
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
7. Broken Pipe
  (1/2 – 48) Hours
8. Advanced Features
9. Reset to Factory Defaults
COMMANDER PRO MENU OPTIONS

## Slide 23
1. Control
  switch or transducer
  set transducer range, drawdown, overpressure, psi setpoint
2. Maximum Motor Current
3. Maximum Frequency
  50 – 80 Hz
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
7. Broken Pipe
  (1/2 – 48) Hours
8. Advanced Features
9. Reset to Factory Defaults
10. Control Settings
  Ramp rate adjustments, transducer calibration
COMMANDER PRO MENU OPTIONS

## Slide 24
COMMANDER PRO MENU OPTIONS
1. Control
2. Maximum Motor Current
3. Maximum Frequency
4. Pass Code Enable
5. Underload Protection
6. Standby Sensitivity
7. Broken Pipe
8. Advanced Features
9. Reset to Factory Defaults
10. Control Settings

## Slide 25
The VFD is operating from and reacting to a short list of measurables:
Voltage
Motor Running Amps
System Pressure (PSI)
Motor Frequency (Hz)
Internal Temp
Cycle Run Time

## Slide 26
Underload protection/fault is normally caused by over-pumping (dry well) condition or pumping against a closed valve.
Underload is triggered by two measurables:
What is Underload Protection?
MOTOR AMPS
MOTOR FREQUENCY

## Slide 27
Underload protection/fault is normally caused by over-pumping (dry well) condition or pumping against a closed valve.
Underload is triggered by two measurables:
What is Underload Protection?
REDUCED RUNNING AMPS
MAXIMUM MOTOR FREQUENCY

## Slide 28
Underload protection/fault is normally caused by over-pumping (dry well) condition or pumping against a closed valve.
Underload is triggered by two measurables:
What is Underload Protection?
REDUCED RUNNING AMPS
MAXIMUM MOTOR FREQUENCY

## Slide 29
When the motor is running at full speed (maximum frequency setpoint) AND below the underload amp threshold the drive will display an Underload Fault.
For example:
TVS15 –
Max Frequency set @ 60Hz
Max Motor Current @ 5.9
Underload Amps default set @ 3.9 (roughly 65% of max, self adjusting)
Underload occurs when motor is running at full frequency of 60Hz and below the 3.9amp threshold.
What is Underload Protection?

## Slide 30
When Underload Fault occurs, the VFD will reset based on the programmed off time in option #5.
This setting is on by default which automatically resets based on run time prior to fault:
The auto reset can be overridden with a specified amount of time –
  15 – 240 minutes, 12hrs or 24hrs
What is Underload off time?

## Slide 31
What is Standby Sensitivity?
MOTOR
AMPS
MOTOR FREQUENCY
SYSTEM
PRESSURE

## Slide 32
The following parameters allow the drive to go into standby.
PSI
Motor Amps
Motor Frequency
All three data points are preset with the assumption that below setpoint operation indicates no flow so drive should go into standby.
PSI – maintained within ½ psi of setpoint
Motor Amps – set @ 3.3 (default for 1.5hp w/max set @ 5.9, self adjusting)
Motor Frequency - below 50 Hz
Conversely, if any one of the data points is higher than preset, the VFD continues to run the system as it recognizes the higher data points correlate to water usage.
What is Standby Sensitivity?

## Slide 33
For example, TVS15 setup on a three phase 1.5hp sub motor set with max current @ 5.9 amps. This preset point (5.9 amps) will automatically generate a standby current in option #6:
PSI – 0.5
  This data point tells the drive that when pressure is within 1/2psi of set point to begin standby operation.
Motor Amps - 3.3 A
  This data point tells the drive that when current is at or below 3.3 amps & pressure is within 1/2 psi of set point to continue standby operation
Motor Frequency – 50Hz
  This data point tells the drive that when motor is operating at or below 50Hz, at or below 3.3 amps and with ½ psi of setpoint to continue standby.
What is Standby Sensitivity?

## Slide 34
A situation can arise where the VFD continues to run at a low load while no water is being used. This will usually result in a broken pipe trip.
There are several contributing factors that cause the drive to run higher than the preset points:
System was sized incorrectly and requires more from pump/motor to make shutoff.
System has changed, such as depleting water table resulting in lower pumping level.
Pump is damaged and not operating at full efficiency
System has developed a leak.
What is Standby Sensitivity?

## Slide 35
System is installed and was sized for 50 psi. End user required more pressure and setpoint is adjusted to 70 psi adding 46’ of TDH.
Default System Parameters:
Frequency below 50Hz
PSI within – 0.5 of setpoint
Current below – 3.3 A
Water is not being used and the display on the VFD shows:
Pressure 70 psi
3.5 A
47 Hz
What is Standby Sensitivity?

## Slide 36
Pressure 70 psi
3.5 A
47 Hz
Standby Parameters:
Frequency 50Hz
PSI – 0.5
Current – 3.3 A
In this case, the standby current needs to be raised above the 3.5 amps required to satisfy pressure setpoint.
Standby current should be raised to 3.7 A
What is Standby Sensitivity?

## Slide 37
VFD SYSTEM TROUBLESHOOTING
Groundwater Support Line
Tony Depew
1-800-628-2313
gwtech@flintandwalling.com