## Slide 1
Water Systems & Accessories Fundamentals

## Slide 3
WATER SOURCE

## Slide 4
Surface
Clay
Sandstone
Shale
Limestone
Sand
Granite
Underground Aquifers
WELL

## Slide 5
Static Water Level
Static Water Level refers to the level of water in a well under
Normal, undisturbed, no-pumping conditions. Static water level is best determined when the well has not been pumped for several hours prior to measuring.
AQUIFERS or UNDERGROUND RESERVOIRS

## Slide 7
PITLESS ADPATERS

## Slide 8
TORQUE ARRESTORS

## Slide 10
Tank Tees
Pressure Switch
20 psi – 40 psi
30 psi – 50 psi
40 psi – 60 psi
WELL

## Slide 11
Terminals
Grounding Screws
Contacts
Pressure Adjustment
Differential Adjustment
Diaphragm
WELL
Pressure Switch

## Slide 12
Pressure Gauge
Check Valve
Boiler Drain
Pressure Relief Valve
Tank Tees
WELL
Pressure Switch

## Slide 13
Sealed Diaphragm
Water
Air

## Slide 14
2-wire Submersible Pump

## Slide 15
3-wire Submersible Pump

## Slide 16
Shallow Well Jet Pump

## Slide 17
Shallow Well Jet Pump
25’ or less

## Slide 18
Deep Well Jet Pump
more than 25’

## Slide 19
What does the Pressure Tank do?
Sealed Diaphragm
Water
Air
It makes the water system i.e. pump cycle “automatic”
With no water in the pressure tank.
RULE of THUMB
Air pressure in the tank needs to be 2-3 lbs. below the “cut in” pressure of the pressure switch..
Air pressure can be checked and adjusted through the snifter valve

## Slide 20
From Pump / Water source
To House / Service
Empty Tank
30/50 Pressure Switch
28 psi
Off

## Slide 21
30/50 Pressure Switch
28 psi
Pump Starts
To Service
Off

## Slide 22
Pressure Tank… How does it work?
38 psi
To Service
Pump Running

## Slide 23
48 psi
To Service
Pump Running

## Slide 24
50 psi
To Service
Pump Shut- off

## Slide 25
50 psi
To Service
Pump Shut- off
Demand for water

## Slide 26
To Service
Pump Shut- off
38 psi
Demand for water

## Slide 27
30 psi
To Service
Pump Starts
Demand for water

## Slide 28
Drawdown (gals)
Amount of water tank provides between pump cycles
Drawdown will vary based on switch settings i.e. Lower the pressure switch setting the more the drawdown

## Slide 29
42 gallon Galvanized Pressure Tank
20 gallon Captive Air Pressure Tank
6.2 gal
30/50 Switch
6.0 gal

## Slide 30
A simple way to size a pressure tank…
Multiply the system requirement (gpm) x 3, then go to the next largest tank.
Example:
8 gpm x 3 = 24 gallons
Part No. 132663 36 gal. tank